# DIVISION 14
LIGHTING

## SECTION 1400

ROADWAY LIGHTING

### 1400-1	DESCRIPTION

Furnish, install, connect and place into satisfactory operating condition lighting at locations shown in the plans.  Perform all work in accordance with the contract and the National Electrical Code.

This division is for methods, materials and equipment to construct and put in working order the proposed lighting; however, every fitting, minor detail, or feature may not be shown or described.  The Contractor shall be an expert in the trade, capable of understanding the intent of the contract and constructing the lighting and electrical system(s) in accordance with the best practice of the trade.

The Contractor actually performing the work described in the contract shall have a license of the proper classification from the North Carolina State Board of Examiners of Electrical Contractors.

Have the licensed Contractor available on the job site as necessary when work is being performed or when requested by the Engineer.  Have this Contractor possess a set of project plans and Specifications on the job site and maintain a set of accurate as built plans.  This Contractor shall be qualified to responsibly instruct and direct all employees regarding the electrical work.

### 1400-2	MATERIALS

Refer to Division 10.

| Item |  | Section |
| --- | --- | --- |
| Conduit |  | 1091-3 |
| Ground Rod |  | 1091-6 |
| Wire |  | 1091-2 |

- General

All materials used in the work are to be new materials unless noted elsewhere in the contract.  References in the contract to any proprietary device, product, material, fixture, form, type of construction, etc. by make or catalog number, with or without the words or approved equal, is to be taken as establishing a standard of quality and is not to be construed as limiting competition.  In such case, the Contractor may use any material, equipment or type of construction which has written approval as being an acceptable equal to that named for the particular use intended by the contract.

Provide materials that are labeled or listed by an acceptable organization, which is defined as an organization that maintains periodic inspection of the production of the materials and verifies, by the labeling or listing procedure, that the materials comply with appropriate standards of performance or are suitable for use in a specified manner.  Provide Underwriters' Laboratories (UL) labeled and listed materials when such labeling and listing is available for such materials.

Make sure that materials are in compliance with requirements for use of domestic products, as specified in other sections of the Specifications.

- Conduit

Use conduit and duct that is either metallic (Rigid Metallic Conduit) or non-metallic (PVC or HDPE), as noted in the plans.

- Wire

Use stranded copper conductors unless specifically noted otherwise on the contract.  Use wire and cable which conforms to IPCEA specifications and has marks for identification (manufacturer's name, type insulation and gauge of conductor) and the UL label.

Use wire insulation rated at 600 VAC or greater.

Use the following types of wiring unless noted otherwise in the plans:

| Service Lateral | UL Type USE |
| --- | --- |
| Control System | UL Type THW or RHW or THHN |
| Feeder Circuits in Conduit | UL Type USE |
| Branch Circuits in Light Standards | UL Type SO Cable |
| Equipment Grounding Conductor | Solid MHD, Bare or Insulated |
| Grounding Electrode Conductor | ASTM B2 |

Use #6 AWG for the grounding electrode conductor unless noted larger in the plans.

- Grounding and Bonding Equipment

Use ground rods which are 5/8" diameter x 10 ft copper clad steel.  Permanently bond grounding conductor to ground rod using exothermic weld.  Make sure that all grounding and bonding equipment conforms to UL Standard 467.

- Fuseholders

Provide fused overcurrent protection in the base of each light standard and other locations as noted.  Use a fuseholder rated at least 600 VAC and 30 A approved for wet locations, constructed so the fuse will be disconnected from the line side power every time the fuseholder is opened.  The fuseholder may be made of molded plastic or rubber and have insulating boots.  Use terminals which are specifically rated for the size and number of conductors required.

Use fuses which have 5,000 A minimum interrupting capacity at the supply voltage, are rated 10 A or as noted in the plans and are not glass type unless specified different in the contract.  Use the same type fuse in all fuseholders on a project unless specified differently at specified locations.

Use fuseholders specifically designed as breakaway devices in fiberglass standards and standards with breakaway bases.  Use fuseholders designed to disconnect line side power without damage to the terminals or conductors every time sufficient pulling force is placed on the line and load side conductors.

- Hardware

Use mounting or attachment hardware including bolts, nuts, washers, straps, clamps and hangers which is made of stainless steel, hot dipped galvanized or of equal corrosion resistance.  Use bolts, which are minimum length and are not less than one nominal size smaller than the opening being used.

- Lamps

Use lamps that conform to ANSI specifications, are of the type and wattage indicated on the contract, are rated for a minimum of 24,000 hours life, have a mogul base and have special coatings for premium efficiency and color rendition.  Provide and install same type lamps for all same type luminaires furnished on the project.

- Duct and Conduit Sealer

Use duct and conduit sealer or mastic which is a putty-like compound and complies with the following:

  - Is permanently non-hardening, non-oxidizing and non-corrosive to metals, rubber, plastic, lacquer and paints;

  - Is readily workable for thumbing into openings and forming into seals around wires inside conduits and openings around conduits;

  - Has a service temperature range of minus 30°F to 200°F;

  - Is clean, non-poisonous and non-injurious to human skin; and

  - Seals against water, dust and air and shall adhere to wood, glass, plastics, metal, rubber and painted surfaces.

- Pull Lines

Place pull lines specifically designed for pulling a rope in all empty conduits and electrical duct so that electrical circuits can be installed in the future.  Use pull lines which are 2 ply with a tensile strength of at least 240 lb and resistant to tangling, rot and mildew.

### 1400-3	SUBMITTALS

- Catalog Cuts

Submit for approval catalog cuts and/or shop drawings for materials proposed for use on the project.  Allow 40 days for review of each submittal.  Do not deliver materials which have not been approved to the project.  Submit 8 copies of each catalog cut and/or drawing and show for each the material description, brand name, stock-number, size, rating, manufacturing specification and the intended use.

Three copies of approved submittals will be returned to the Contractor.  Present a catalog cut or drawing for all components of each contract item.  Present the submittals neatly arranged in the same order as the contract bid items.

- Certifications

Furnish a Type 3 material certification in accordance with Article 106-3 for light standards, high mounts and lowering devices and a Type 6 material certification for conductors.  Submit certifications when the above materials are delivered to the project.

Type 3 or Type 6 material certifications in accordance with Article 106-3 may be requested for any or all of the other material which does not have a name plate showing sufficient information to verify that the material was manufactured to the requirements of this section.

- Samples

Random samples will be taken of the various items for the purpose of verifying conformance with Specifications.  The selection of the items to be sampled and the taking of the samples will be done by the Engineer.

Failure to meet specification requirements by 2 samples of any material will be sufficient reason for rejection of all materials from the same lot.

Upon request, there will be reimbursement for the actual verified cost of such material taken as samples, including any handling charges less any discount allowed on the invoice, but with no percentage added, and such material will thereafter become the property of the Department.

- As-Built Plans

Submit 2 complete sets of as-built plans for review upon completion of the work, showing the location of all buried electrical circuits, with pavement crossings dimensioned from fixed objects or from survey stations.

Include in the as-built plans the title (No. 1), index (No. 1A), summary of quantities (No. 3) and all of the layout and detail (E) sheets of the project with all changes indicated.  After review and approval, place one set of these as-built plans in a waterproof envelope and file in each control panel.

Submit one set of as-built plans to the Roadway Design Unit.

Show the light standard foundations that are relocated (by permission of the Engineer) on the as-built plans in their final locations.

Keep a daily record of the location of all items in order to ensure the accuracy of the 
as-built plans.

- Warranties

Turn over warranties from each manufacturer of electrical materials and equipment pertinent to the complete and satisfactory operation of the system before the acceptance of the project.  Indicate the expiration date on each warranty furnished.  The warranty shall not be less than those provided as a customary trade practice.

- Computations and Welding Procedures

Submittals of structural design computations and drawings showing material and welding specifications, as required in other sections of the Standard Specifications such as High Mount Standards, may require 10 weeks for review.

### 1400-4	CONSTRUCTION METHODS

- Location Surveys

All light standards, high mount foundations and electrical duct will be located unless indicated differently elsewhere in the contract.  Mark the proposed location of circuits, circuit markers, control systems, service poles, junction boxes, luminaires and all other components for approval before installation.

The plan locations of the light standards and high mounts may be adjusted to be behind guardrail, to avoid obstructions or to avoid undesirable foundation conditions.  Ensure location changes are approved before construction.  Light standards can be moved no more than 10 ft longitudinally and 2 ft laterally unless approved by the Special Design Section of Roadway Design Unit.  High mast light standards can be moved no more than 25 ft radially unless approved by the Special Design Section of Roadway Design Unit.

Verify project dimensions on the site, actual measurement always taking precedence over scaled plan dimensions, with every part of the work fitted to actual conditions at the site.

- Damage to Facilities

Take all precautions necessary to avoid damage to existing underdrains and other buried facilities located in certain areas.  Hand trenching may be required to avoid damage to the underdrains, storm sewer systems and other facilities.  Construct light pole foundations with a minimum horizontal clearance of 10 ft to storm sewers or other underground installations which might affect the foundation stability.  Make lateral and longitudinal changes in pole locations in the field to provide the required clearance, as directed.

Trenching and construction operations may require the removal of, or result in damage to, existing shoulders and paved ditches.  Restore all disturbed portions of the project to their original condition or as approved.

Installation of conductors may require trenching through existing guardrail locations.  Trenching may be done beneath the guardrail in a manner that will not disturb the guardrail installation or the Contractor may remove short sections of guardrail to facilitate mechanical trenching.  Reinstall all removed guardrail by the end of the day's work.  Permission is required before removal of any guardrail.  Repair any damage to the guardrail installation or to the galvanizing of the material as directed.

Repair all trenched, excavated, or otherwise damaged earth surface areas by shaping, smoothing, seeding and mulching the damaged areas as required by the Specifications and as directed.

- Existing Utilities

Water, sewer, telephone, fire alarm, traffic signal and power lines may be located in the same area that lighting standards and circuits are to be installed.

Locate these lines before operations are begun.  Field changes approved by the Engineer may be made to provide clearance required by the NESC.

Foundations or other construction which is installed in conflict with existing utilities will not be acceptable.  Remove unacceptable conflicting construction and repair damage to utilities at no cost to the Department.

When the work involves replacing or renovating existing lighting, make all reasonable efforts to prevent dark spots in the lighting system.  Phase lighting construction to allow existing lighting to remain in operation as long as possible.

- Operation of Equipment

Use a bucket truck to raise workers into position to install and/or adjust luminaires and lamps after the initial setting of the standards.  Taking down the light standard to check or make adjustments at the top is not allowed.

Install all bore pits outside the clear zone.

- Conduit Installation

Install conduit continuous, watertight, free of kinks and make all runs with as few couplings as standard lengths will permit.  Do not exceed a total angle of 270° between outlets unless otherwise approved.  Conduit bodies with covers and neoprene gaskets may be used to facilitate the installation of the wires at locations indicated in the plans.

Provide protection at all times against the entrance of water or other foreign matter into the conduit.  Plug or cap conduit when work is temporarily suspended, including nightly stoppage of work.

Clean all conduits before installation and upon completion of the system.  Snake an approved cleaner with a diameter not less than 85% of the nominal diameter of the conduit through each conduit before installing the wire.

Install the conduit in such a manner that temperature changes will not cause elongation or contraction that might damage the system.  Provide expansion fittings where conduit crosses structure expansion joints and at other locations shown in the plans.

Avoid short radius bends in non-metallic conduit to prevent burn-through of the pulling cable or conductors during pulling operations.

Install caps or plugs on stub-outs for future use.  Caps and plugs shall be made of the same material as the conduit.  Where non-metallic conduit is joined to metallic conduit, use a transition adapter.  Install bushings on all conduit ends projecting into panels, boxes, or other enclosures.  Provide pull lines in all conduits for future installation of circuitry.  Coat field cut threads and other uncoated metal or damaged galvanizing with organic zinc repair paint.  Securely fasten conduit.  For the spacing of fasteners, do not exceed 4 ft for 1 1/2" conduit and larger or 6 ft for 1 1/4" conduit and smaller.  Use fasteners that are hot dipped galvanized or stainless steel.  Provide backs with all conduit straps installed on flat surfaces.  Rotary-impact drills may be used for installing expansion anchors in concrete.  Do not use powder explosion type units.

Do not install underground conduit until the area has been brought to final earth grade.  Give careful attention to the vertical and horizontal alignment of the conduit to provide the smoothest installation.

- Wiring Methods

Do not pull wire through a conduit system until the system is complete and has been cleaned.  Use approved wire pulling lubricants.  Pull conductors by hand, or use motorized cable-pulling equipment designed for pulling multiple cables into conduit.  Use sheaves or rollers, as required to prevent damage to conductor insulation.  Do not use an automobile to generate cable pulling forces.  Use equipment similar to the Greenlee model UT2 cable pulling system, or Engineer approved equal.

Color code all conductors per the NEC (grounded neutral is white, grounding is bare or green) and use phase conductors which are black and red.  Approved marking tape, paint, or sleeves may be used instead of continuous colored conductors for No. 8 AWG and larger.  Do not mark a white conductor in a cable assembly any other color.  White, red or black conductor may be stripped at all accessible points and used as a bare equipment grounding conductor.

Joints, taps and splices will only be permitted at locations indicated in the plans and by the following method.

Install a manufactured set screw type connector, suitable for connecting multiple wires and are UL Listed (UL486D).  These precise fit connectors are insulated with high-strength dielectric material and equipped with factory made waterproof insulating boots and removable access plugs over the set screws.  These connectors are suitable for use in direct burial and submersible applications.  Tape down the access plugs to keep them securely in place.  Split-bolt, wire nut and compression type connectors will not be allowed.

All splices inside light standards shall be easily accessible through handholes unless standard is mounted on breakaway transformer base.

- Grounding Electrodes

Install grounding electrodes at each light standard, high mast light standard and control system as shown in the plans.  The rod shall be driven vertically until the top is 6" below the ground surface.  The grounding conductor must be connected to the grounding electrode by exothermic weld.

- Equipment Mounting

Mount equipment securely at locations shown in the plans in conformance with the dimensions shown and make vertically plumb and level.  Install fasteners as recommended by the manufacturer and space evenly.  Use all mounting holes and attachment points for attaching enclosures to structures.

- Base Protection

For median mounted light standards, use a protective metal shroud installed underneath the light standard base plate to protect the exposed anchor bolts and lighting circuitry segments between the base plate and the top of the concrete median barrier.  The metal shroud shall be fabricated of either galvanized steel, minimum gauge 22, or aluminum, minimum gauge 18, to match the material type of the light standard.  The metal shroud shall be composed of 2 overlapping pieces, and attached with 2 self-tapping stainless steel or galvanized machine screws at each overlap point.

For high mount standard, use galvanized steel welded wire reinforcement between the top of foundation and bottom of mounting base.  Attach welded wire reinforcement to anchor bolts with size AWG 14 copper wire or small gauge galvanized wire.

- Galvanizing Repair

Repair any damaged galvanized components in accordance with Article 1076-7.

### 1400-5	ELECTRICAL INSPECTIONS AND TESTING

Comply with all local ordinances and regulations.  Apply for and obtain all permits and/or licenses required by local regulation.

Provide a calibrated MegOhmMeter, with certification that calibration was done within one year of use.  Provide a meter manufactured by Fluke, Amprobe, Biddle or Engineer approved equal.  Present the meter for inspection, at the Pre-Lighting-Work meeting described in Section 1400-11.

During project construction the Contractor will perform an insulation resistance test on each feeder circuit conductor.  The insulation resistance for each conductor shall exceed 5 megaohms after charging for 30 seconds at 500 VAC or 1000 VDC.  A copy of the Contractor Meg Circuit Data Form is available on the Roadway Design Unit website.  The data form will be completed by the Contractor and submitted to the Lighting and Electrical Squad of the Roadway Design Unit for review before final inspection.

If the insulation resistance test of any conductor indicates a value of less than 5 megaohms, locate the fault.  If the fault is in a conductor between terminal connections, replace the conductor.  If the fault is at a terminal connection, repair or replace the terminal device.

Removing water from the conduit of a faulty circuit is not considered a repair.  Water in the conduit allows electric current to flow between skinned places in the conductors insulation.  If a circuit fails the insulation resistance test and removing water allows the circuit to pass, replace the conductors and re-test the new circuit.

After all control system cabinet wiring has been installed and connected in the proposed permanent manner the Contractor will contact the Office of State Fire Marshall of the Department of Insurance, or local authority having jurisdiction, to perform an electrical inspection of the lighting system.  Upon satisfactory testing, the Contractor will be issued a Certificate of Inspection for the lighting system.  The Contractor may then arrange with the power company to provide the necessary power service.  The Certificate of Inspection will be turned over to the Engineer before project acceptance.  Inspection by local authorities will neither eliminate nor supersede the final inspection by the Engineer to ensure compliance with the contract.

Have all work inspected and approved by the Engineer before concealment.  An inspection will be made during the progress and after the work has been completed.  It will also include an inspection made at night to determine the optical qualities of each luminaire.  Adjust all luminaires having unsatisfactory qualities as directed.

Provide the necessary personnel and equipment for aiming luminaires during nighttime inspections by the Engineer.

The Engineer should contact either the Special Design Section or the Lighting and Electrical Squad of Roadway Design Unit to schedule a final inspection of lighting systems at least 2 weeks before the requested inspection date.  The Lighting and Electrical Squad will perform an insulation resistance test as described above, inspect the system for adherence to contract requirements and prepare a lighting inspection memo based on the Lighting System Inspection Checklist.  A copy of the inspection checklist is available on the Roadway Design Unit’s website.  The Contractor is responsible for providing the personnel and equipment necessary for removing and replacing fuseholders and/or operating circuit breakers to facilitate the insulation resistance test performed by the Lighting and Electrical Squad.

### 1400-6	BURN-IN TEST

After all the issues mentioned in the lighting inspection punchlist are addressed to the satisfaction of the Engineer, the lighting system will undergo a 2-week burn-in test.  The burn-in test consists of normal dusk to dawn operation of all lighting system control equipment and apparatus, without interruption or failure attributable to poor workmanship or defective material.  At the end of the burn-in test, all lights and equipment will be inspected for normal operation.  The Contractor will make any necessary repairs or replacements at no cost to the Department.

Conduct the burn-in test at the same time for all lights which are energized from the same utility company service point.

Burn-in tests of individual circuits or groups of lights will not be acceptable.

### 1400-7	IDENTIFICATION

Identify each component of the lighting/electrical system as indicated in the plans.  Use a method of identification which includes an approved paint, adhesive label, heat shrink label or embossed concrete.  Label conductors on components requiring identification at each terminal, circuit breaker, light standard, high mount standard, control system, junction box and underpass panel.

Label each circuit conductor at each terminal and access point with the circuit number indicated in the plans.

Identify light standards and high mount standards by the control system and location number indicated in the plans.  Put the identification on the front side of the standard facing the traffic at a height of 6 ft above ground level.  Identify control systems and underpass panels on the exterior of the front panel.

### 1400-8	LOCKS AND KEYS

Supply all access doors to control cabinet enclosures with locks that meet the Engineer's approval.  Key all locks alike and furnish 8 keys to the Engineer.

### 1400-9	ELECTRICAL SERVICE

Coordinate all work to ensure that electrical power of the proper voltage, phase, frequency and ampacity is available to complete the project.  Contact the utility company, make application, pay all deposits and other costs to provide necessary electrical service.  The Contractor will be reimbursed for the actual verified cost of any utility company charges.

The Engineer will provide authorization to the Contractor for electrical service to be obtained in the name of the Department and for the monthly power bills to be sent directly from the utility company to the Department.  The Department will be responsible for direct payment of monthly power bills received from the utility company.

### 1400-10	TERMINOLOGY

The terms “High Mast” and “High Mount” are used synonymously in the contract.

The term “By Others” means work to be accomplished and paid under contract items other than those clearly pertaining to the work specified or shown.  Work by others may be included in this contract for the Contractor to provide, or it may be provided under another contract or by someone other than the Contractor.

Abandon means that the materials will not be used in the final completed form of the work.  Remove all abandoned materials from the project or terminate at least 18" below subgrade so they will not be in conflict with the finished project.

### 1400-11	CONSTRUCTION PHASING

Schedule a Pre-Lighting-Work meeting before beginning work on the lighting system.  Include staff members from the prime contractor, electrical sub-contractor, Resident Engineer’s office and the Lighting and Electrical Squad in the Roadway Design Unit in Raleigh

Accomplish lighting work along with other roadway construction in the appropriate phases as indicated in the Traffic Control Plans and these Specifications.

### 1400-12	MEASUREMENT AND PAYMENT

There will be no direct payment, except where specifically noted in the Subarticle 1400-3(C) and Article 1400-9 for the work required in the preceding sections of this division.  Payment of the contract unit prices for the various items in the contract will be full compensation for all work required.

1400-13	CONTRACTOR MEG CIRCUIT DATA FORM

The Electrical Sub-contractor is responsible for completing the Meg Circuit Form and submitting the insulation resistance data to the Lighting and Electrical Squad of Roadway Design Unit for review before final inspection.  A copy of the Contractor Meg Circuit Data Form is available on the Roadway Design Unit’s website.

1400-14	LIGHTING SYSTEM INSPECTION CHECKLIST

The Engineer is responsible for scheduling the lighting system final inspection by contacting either the Special Design Section or the Lighting and Electrical Squad of the Roadway Design Unit.  The Lighting and Electrical Squad will coordinate with project inspector and electrical subcontractor to have the checklist items inspected during the final inspection and in preparation of the lighting inspection punchlist.  A copy of the inspection checklist is available on the Roadway Design Unit’s website.

## SECTION 1401

HIGH MOUNT STANDARD

1401-1	DESCRIPTION

Design, furnish and install a high mount standard 60' or greater in height with a top-latched lowering device and portable drive unit including the drive, winch, wiring, cables, brackets, hardware, transformer, power cord, storage case and operating manuals.

### 1401-2	MATERIALS

- High Mount Standard

Provide certified computations and fabrication drawings by a professional engineer licensed in the State of North Carolina.

Design the support including base plate and anchorage in conformance with the AASHTO Standard Specifications for Structural Supports for Highway Signs, Luminaires and Traffic Signals, Fourth Edition, 2001 and the Interim Specifications valid at the time of letting.  Use Fatigue Category II.  Design and fabricate welds in accordance with Article 1072-18.  Design the support for the wind velocity shown in the plans.

Have the drawings show all details relating to pole, access hole, base, anchorage and lowering device.  Show references to ASTM specifications or to other material specifications for each type of material used on the drawings.  Note the total weight in pounds on the drawings for each component and the total assembly.  Make sure that all drawings are clearly identified with a drawing number and signed and dated by the manufacturer's authorized representative.

Show clearly full and complete information regarding location, type, size and extent of all welds on the drawings.  For groove welds, indicate the particular detail and process to be employed in production of the work.  For prequalified joints, use of the Structural Welding Code - Steel, AWS D1.1 letter classification designation of the 
joint (B-L2b-S, etc.) will satisfy this requirement.

The standard may be either a multisided or round tubular member.

The criteria listed below shall apply to 60-ft, 80-ft, 100-ft and 120-ft high mount light poles:

  - Provide 8 or more anchor rods for each pole.

  - Provide base plate thickness of at least 2.5".

  - Provide welded wire reinforcement for base protection that meets 
Subarticle 1400-4(I).

Furnish 8 copies of complete detailed drawings and one copy of the complete design computations for each height of standard for approval before fabrication.

The Contractor's attention is directed to the fact that it will take 10 weeks to secure approval after submission of the complete drawings and computations.

Fabricate the support in accordance with the details shown on the approved shop drawings and the Specifications.

Test all base plate to upright welds using magnetic particle testing (MPT) before galvanizing.  All base plates must be tested at 100%.  Radiographically test the longitudinal seam welds within 6" of circumferential welds in the outer tube of the slip fit joint area.

Hot dip galvanize metalwork after fabrication has been completed.  Ensure the galvanization conforms to ASTM A153 for fasteners and ASTM A123 for other structural steel.

Partial penetration longitudinal groove welds on shaft sections, having a minimum throat of 60% of the thickness of material being joined, will be acceptable provided the qualification requirements of the Structural Welding Code - Steel, AWS D1.1 are met.  However, full penetration will be required on longitudinal groove welds within 6" of circumferential welds and in areas where a shaft section telescopes over another shaft section.  No field welding of any part of the assembly will be permitted.

Allow easy access to all components in the base of the standard with a hand hole with a hinged and lockable door.  Allow for opening of the door without the use of special tools or wrenches.  Make the hand hole large enough for removal of the circuit breaker and the hoist gearbox and winch assembly (at least 9" x 18".)  Make the door hinge and lock mechanism sturdy enough to prevent vandalism and to prevent freeze-up or binding due to corrosion or too tight fit.  Achieve locking with a conventional padlock.  Built-in locks or latching mechanism for the door will not be acceptable.

- Lowering Device

Furnish 8 copies of complete detailed drawings of the lowering device with manuals describing the assembly, erecting and operating procedures.  Include precise instructions on stringing the cables and leveling the carrier ring.

Each high mount lighting standard shall have a device to lower the luminaires from the operating position at the top of the standard to a service position approximately 3 ft above the base of the standard.  Include on the device a head-frame, top latching carrier ring and winch assembly.  Design the lowering device for the number of luminaires as shown in the plans, each weighing and each having a projected area in accordance with Section 1403.

Mount the head frame on the standard with a slipfitter and set screws, and have sheaves or rollers for the lifting and power cables.  Ensure sockets automatically secure the carrier ring at the top in the raised position and provide a hood on the entire assembly for protection from the weather.  Attain latching and unlatching by alternately raising and lowering the carrier ring.  Use sheaves that are non-corrosive materials with bronze bushings and stainless steel shafts.  Provide suitable retainers to assure that the cables stay in correct position.

Have slipfitter tenons equally spaced for mounting the luminaires on the carrier ring.  Have the carrier ring automatically latched to the head frame when raised into position by suitable pins and sockets which will prevent the luminaires from swaying, turning, vibrating, or otherwise moving out of proper position.  Include on the carrier ring spring loaded roller arms to guide the ring during raising and lowering operations.  Use springs made of stainless steel and rollers made of nylon.  Mount a metal NEMA 3R weatherproof junction box on the ring for connection of individual luminaire circuits to the electrical power supply cable.  Include in the junction box a flanged inlet for connection of the power supply cable.  Use an inlet and cable connector which is of the locking type and weatherproof.

Use a winch assembly that is a self-locking worm gear type designed for operation with a portable power unit.  Have the winch drum automatically reverse the lay of the hoist cable and prevent uneven build-up or tangling.

Provide a terminator for joining the hoist cable and 3 suspension or lifting cables.  Provide the means to compensate for variations in the lengths of the 3 lifting cables.  Use hoist and lifting cables made of stranded high strength stainless steel extra flexible aircraft type.  Use hoist and lifting cables that meet structural requirements of Military Specification MIL-W-83420E and have the center strand not protruding more than 0.06" after the cable is cut.

Use a power supply cable that is rated for suspension and has approved strain relief fittings at each end.  At the base of the standard, provide a locking type plug with waterproof cover to connect to a short power supply cable stubbed from the circuit breaker panel.

- Portable Drive

Supply a portable drive unit with a heavy duty reversible electric motor with torque limiter type drive of adequate capacity, complete with a grounding type cord, suitable couplings for attaching the unit to the winch assembly, and a sturdy storage container for the unit and accessories involved.  Provide one portable drive unit for the completed project.  Provide a drive unit with a lever switch controller with clearly marked up and down positions.  Connect the controller to the drive unit with a cord of sufficient length to let the operator stand a minimum of 15 ft from the base of the high mount during lowering or raising operations.

Shop assemble the portable drive unit and remove all rough edges.  Use mounting or adjustment bolts which allow hand tightening.

Provide a complete unit that includes a durable metal storage case with all equipment and instructions for operation.  Use a case which is the approximate size as shown in the plans, has a continuous hinge on the lid, and has sturdy carrying handles on each end.  Furnish a hasp with padlock as shown in the plans.  Construct the case with 16 gauge formed and welded steel with bracing to prevent warping.  Paint the inside and outside with a durable quality paint.  Provide an identification label as noted in the plans on the storage case.

- Circuitry

Install an enclosed circuit breaker in the base of the high mount standard.  Use a breaker which is rated 480 VAC, 2 pole, 30 A, and a minimum interrupting capacity of 14,000 A unless noted otherwise in the plans.

Provide a supply cord originating from the circuit breaker with a female twist lock connector for testing the luminaires at ground level, during lowering operation using the portable drive unit and when in the raised position during normal night operation.

Provide a junction box mounted on the lowering ring with a flanged inlet to accept the female twist lock connector from the supply cord.  Use plugs, flanged inlets and connectors for the supply cable and drive unit which allow grounding and are weatherproof.

Install the wiring for each high mount luminaire separately from the luminaire to the junction box.  Series or loop circuitry is not allowed.

Provide a transformer, branch circuit breaker and GFCI receptacle as a power source for the portable drive.

Provide an equipment grounding conductor in the supply cable.  Include an equipment grounding conductor in the wiring for each luminaire.

- Operation

Demonstrate the operation of the lowering device by raising and lowering the carrier ring with luminaires a minimum of 5 times for each high mast.  Include in this demonstration latching and unlatching at the top and connection of test cables at the bottom.  Twisting of the cables, failure of the carrier ring to latch or unlatch, unlevelness of the carrie or hang-up of guide arms will be sufficient reason not to accept the lowering device.

### 1401-3	CONSTRUCTION METHODS

Use suitable blocking and slings to prevent warping of the high mount standard during storage and transportation.  Assemble all parts and string all cables in strict accordance with the manufacturer's instructions.

Make sure that the top of the standard is not out of plumb more than 0.5% of its height.

Include assembly instructions and any special tools, blocks, washers, etc. in the portable drive storage case.

Remove all dirt, stains, marks, etc. before erecting the high mast.

### 1401-4	MEASUREMENT AND PAYMENT

High Mount Standards with lowering devices to be paid will be the actual number of standards installed and accepted.  High mount lighting standards with lowering device, measured as provided above, will be paid at the contract unit price each for ____ High Mount Standard of the appropriate height.

Portable Drive Units with storage cases to be paid will be the actual number of portable drive units furnished and accepted.  Portable drive units with storage case, measured as provided above, will be paid at the contract unit price each for Portable Drive Unit.

Payment will be made under:

| Pay Item |  | Pay Unit |
| --- | --- | --- |
| ____ High Mount Standard |  | Each |
| Portable Drive Unit |  | Each |

## SECTION 1403

HIGH MOUNT LUMINAIRES

1403-1	DESCRIPTION

Furnish and install luminaires, including lamps and ballasts, for high mount standards 60 ft and greater in height.

### 1403-2	MATERIALS

Provide luminaires consisting of a die cast aluminum ballast housing a cast aluminum slipfitter housing, and cover which do not weigh more than 65 lb and have an effective projected area not more than 2.5 sq.ft.

Provide ballast capable of operating a high pressure sodium lamp from a source with a nominal voltage as shown in the plans with a tolerance of ± 10%.  Provide luminaires with IES Distribution, Cutoff, Type V and the wattage shown in the plans.  The Department will evaluate photometric data for submitted luminaire to ensure adequate light output from the fixture.

Provide slipfitter housing suitable for use with 2" horizontal mounting, adjustable for leveling, and which secures the mounting assembly to prevent twisting of the luminaire about the bracket.

Use an optical assembly which contains a porcelain enclosed mogul socket with spring loaded center contact .  Position the socket for base up lamps.

Provide complete photometric, assembly and electrical data for each type luminaire proposed.  Include in the data candlepower distribution and isofootcandle graphs, assembly drawings with replacement part numbers and electrical schematic with ballast input, output, voltage, amperage and wattage ratings.

Provide same model lamps from same manufacturer for each respective luminaire type.

### 1403-3	CONSTRUCTION METHODS

Lamp all high mount fixtures just before testing the system.

Level and secure each luminaire in all directions.  Careful attention should be given to aim the main beams and house-side outputs of all asymmetrical units in the direction indicated in the plans.  Securely terminate the wiring for each luminaire and include an equipment grounding conductor to bond the housing to the supply cord grounding conductor.

### 1403-4	MEASUREMENT AND PAYMENT

High Mount Luminaires ____ of the appropriate wattage and type will be measured and paid as the actual number of luminaires of each size and type installed and accepted.

Payment will be made under:

| Pay Item |  | Pay Unit |
| --- | --- | --- |
| High Mount Luminaires ____ |  | Each |

## SECTION 1404

LIGHT STANDARDS

1404-1	DESCRIPTION

Furnish and install light standards less than 55 ft high complete with bracket arm(s), including the impact attenuation device (breakaway base) as shown in the plans.

### 1404-2	MATERIALS

Provide a standard that meets the design criteria of the AASHTO Standard Specifications for Structural Supports for Highway Signs, Luminaires and Traffic Signals and the Interim Specifications valid at the time of letting.  The support is to be designed for the wind velocity shown in the plans.

Provide a standard designed to support an ellipsoidal shaped luminaire, which has a center of gravity not more than 18" from the end of the support, with a minimum weight and projected area and a bracket arm length as indicated in the contract.

Make sure that each lighting standard has a grounding lug in the standard located within 6" of the handhole or in the transformer base.

Deliver standards with a smooth uniform finish, free of disfiguring scratches or dents and with suitable protection for further handling during erection.

Wrap or package each light standard as recommended by the manufacturer to prevent damage during shipping and handling.  Repair or replace, at the option of the Engineer, any standards with abraded finishes or other damage.

Furnish aluminum or steel standards and arms; however, use the elected material throughout the project.

Galvanize steel components after fabrication.  Use galvanization which conforms to the requirements of ASTM A123 for tubes, plates and bars and to ASTM A153 for hardware.

Use connecting bolts, washers and nuts compatible with the transformer base as recommended by the light standard manufacturer and which comply with the contract.

Use anchor bolts, washers, nuts and shims which comply with the Specifications and details shown in the plans as recommended by the light standard and transformer base manufacturer(s).

Furnish anchor and/or connecting bolt covers and pole top caps with standards as indicated in the plans.

Provide pole hardware such as nuts, bolts and washers for aluminum standards from 
18-8 stainless steel or aluminum alloy 2024-T4.  Provide nuts, bolts and washers for steel standards from 18-8 stainless steel or steel conforming to ASTM A307.  Submit drawings for approval which show material specifications for each component.

Use bracket arms for each standard which are the length shown in the plan sheet and of the same material as the standard.

Provide light standards with an approved impact attenuation feature (breakaway base) that complies with AASHTO Standard Specifications for Structural Supports for Highway Signs, Luminaires and Traffic Signals and one of the following descriptions:

- A cast aluminum transformer base,

- A frangible base insert or adapter, or

- A slip base.

Use the same type of breakaway device throughout the entire project.  All breakaway devices shall be FHWA approved.  Include in the device protection for wiring and conduit at the base of the standard, in the form of a special heavy-formed material secured in place.

### 1404-3	CONSTRUCTION METHODS

Locate and number the light standards as shown in the plans.

Do not lay the standards on the ground without proper blocking and protection to prevent warping and discoloration.  Protect the standards from damage by other construction work, including landscape mulching and fertilizing operations.

Securely mount the standards on the anchor bolts, and plumb up with nuts torqued according to the manufacturer's recommendation.

Mounting height is defined as vertical distance from luminaire to surface of pavement of heaviest traveled lane in area illuminated by the luminaire.  A tolerance of ± 1.5 ft from the required mounting height will be permitted.  If this tolerance is exceeded, furnish and install an acceptable standard within this tolerance.

### 1404-4	MEASUREMENT AND PAYMENT

Light Standards, ____ will be measured and paid as the actual number of light standards with arm assemblies of each appropriate mounting height and bracket arm type and length installed and accepted.

Payment will be made under:

| Pay Item |  | Pay Unit |
| --- | --- | --- |
| Light Standards, ____ |  | Each |

## SECTION 1405

STANDARD FOUNDATION

1405-1	DESCRIPTION

Furnish and install all materials necessary to construct concrete foundations for light standards, including concrete, reinforcing steel, anchor bolts, nuts, forms, excavation and backfilling.

### 1405-2	MATERIALS

Refer to Division 10.

| Item |  | Section |
| --- | --- | --- |
| Conduit |  | 1400-2(B) |
| Metal Shroud |  | 1400-4(I) |
| Portland Cement Concrete, Class A |  | 1000 |
| Reinforcing Steel |  | 1070 |

Provide Type 3 material certifications in accordance with Article 106-3 for conduit and anchor bolt assemblies.  Store steel materials on blocking at least 12" above the ground and protect it at all times from damage; and when placing in the work make sure it is free from dirt, dust, loose mill scale, loose rust, paint, oil or other foreign materials.  Load, transport, unload and store foundation and anchor bolt assembly materials so materials are kept clean and free of damage.

Provide anchor bolt assemblies in accordance with Roadway Standard Drawings No. 1405.01 consisting of the following:

- Straight anchor bolts or anchor bolts with hooks;

- Heavy hex nuts, leveling nuts, flat washers and lock washers on exposed ends of bolts; and

- Nuts and flat bars on the other ends of straight anchor bolts embedded in concrete.

Use steel anchor bolts, nuts and flat washers that meet ASTM F1554 for Grade 55 bolts and Grade A nuts.  Provide steel lock washers.  Galvanize anchor bolts and exposed nuts and washers in accordance with Article 1076-4.  It is not necessary to galvanize nuts and bars embedded in concrete.

### 1405-3	CONSTRUCTION METHODS

The foundation design shown in the plans is based upon placing foundations into undisturbed soil or fill of at least medium density.  The Engineer will stake each location and determine the top of foundation elevation unless indicated differently elsewhere in the Specifications.  The foundation type and depth will be determined by the plan details in accordance with the final soil and slope conditions at each location.  Set anchor bolts in accordance with stub height requirements on the Roadway Standard Drawings No. 1405.01.

Pour the concrete for the pedestal portion monolithic with the barrier portion on light standard foundations that are an integral part of a barrier.  Construct the barrier portion as specified in the contract and continuous through the foundation.  Coordinate construction of foundations in median barrier with the signing plans to avoid conflict with overhead sign structure foundations.

Where rock creates a conflict with construction of the standard foundations, an alternate foundation may be constructed if approved.

Install aground rod adjacent to the light standard foundation and permanently attach grounding conductor from standard.

### 1405-4	MEASUREMENT AND PAYMENT

Standard Foundation ____ will be measured and paid as the actual number of foundations for each appropriate height and type of standard, completed and accepted.

The quantity of bedrock foundations to be paid will be the actual number of alternate foundations for bedrock locations for standards of the appropriate type, installed and accepted.

Alternate foundations for rock locations will be paid at 1.5 times the contract unit price each for Standard Foundations, ____ of the appropriate type that would have been installed if rock had not been encountered.

The requirements of Article 104-5, which pertain to adjustments in contract unit prices for overrunning or underrunning pay items, will not be applicable to pay items covered by this section.

Payment will be made under:

| Pay Item |  | Pay Unit |
| --- | --- | --- |
| Standard Foundation, ____ |  | Each |

## SECTION 1406

LIGHT STANDARD LUMINAIRES

1406-1	DESCRIPTION

Furnish, install and place into satisfactory operation, luminaires on the bracket arm complete with all lamps, ballasts, wiring inside standard from circuit conductors to luminaire, in-line breakaway fuses and ground wiring at the pole on light standards less than 55 ft in height.

### 1406-2	MATERIALS

Use luminaires that are ellipsoidal shaped with a center of gravity not more than 18" from the end of the luminaire support, do not weigh more than 55 lb, and have a maximum effective projected area of 1.2 sq.ft.

Use luminaires that are UL listed and labeled.

Use luminaires that have a lens holder latch on the street side and ballast, plug-in starter and capacitors mounted on a removable door.  The removable door shall have a continuous hinge bar to prevent door opening due to vibration.  The luminaire shall have a slipfitter for 2 mounting brackets, with a stainless steel shield ring, a 4-bolt adjustable pipe clamp and leveling steps for tilt adjustment.  Use luminaires with a replaceable mogul base lamp socket adjustable in both vertical and horizontal directions, capable of producing the specified IES distribution pattern.  Third party certification for photometric data shall be provided upon request.  Provide a heat resistant tempered flat glass lens and a reflector with a hard glasslike highly reflective corrosion resistant finish.  Provide a filter between the lens and reflector tub.

Use luminaires that have an internal high power factor ballast of the regulated type, capable of operating from a multi-wire circuit and energize a high intensity discharge lamp.  The luminaire shall have a barrier between the ballast compartment and the reflector tub.  Transformer windings shall be covered and protected.  Lamps shall operate satisfactorily with a line voltage variation of ± 10%.  Provide a ballast pre-wired to the lamp socket and terminal board, requiring only the connection of the power supply leads to the terminal board.

Use luminaires with a wattage rating, voltage rating, lamp type and light distribution as indicated in the plans.

Provide same model lamps from same manufacturer for each respective luminaire type.

### 1406-3	CONSTRUCTION METHODS

Level luminaires using leveling pads on the luminaire enclosure.  Adjust any luminaires, as directed, to give optimum illumination distribution.

### 1406-4	MEASUREMENT AND PAYMENT

Light Standard Luminaires ____ will be measured and paid as the actual number of luminaires of each appropriate size and style installed and accepted.

Payment will be made under:

| Pay Item |  | Pay Unit |
| --- | --- | --- |
| Light Standard Luminaires ____ |  | Each |

## SECTION 1407

ELECTRIC SERVICE POLE AND LATERAL

1407-1	DESCRIPTION

Furnish and install wood service poles, wire, conduit, bushings, fittings, connectors, meter base and weatherhead from the service point to a control system.

### 1407-2	MATERIALS

Refer to Division 10.

| Item |  | Section |
| --- | --- | --- |
| Wood Poles, Class 4 |  | 1082 |
| Type USE Wire |  | 1091-2, 1400-2 |
| Conduit |  | 1091-3 |

### 1407-3	CONSTRUCTION METHODS

Dig holes large enough to permit the proper use of tampers to the full depth of the hole.  Place backfill in the hole in 6" maximum layers and thoroughly tamp.  Place surplus earth around the pole in a conical shape and pack tightly to drain water away.

Set the pole to a depth of at least 5.5 ft unless shown otherwise in the plans.  When utility power is available from outside the right of way, locate the service pole no more than 10 ft inside the right of way.  The utility company will install overhead conductors from their facilities.  Install an underground service lateral from the service pole to the control system.  The proposed service pole will be deleted from the contract if the utility company:

- Provides a pad mount transformer,

- Allows attachment of the riser and weatherhead to their pole, or

- Provides underground service from their pole.

Make connections at the service head at the bottom of the drip loop to prevent siphoning of water through the cable.

Provide for a meter in accordance with the requirements of the utility company's condition of service.  A meter base for a self-contained meter may be mounted on the service pole or back of the control enclosure as indicated in the plans.  A current transformer (CT) cabinet and meter base may be mounted in either location if requested by the utility company.

Use stranded copper Type USE conductors installed in rigid galvanized steel conduit sized as shown in the plans for the service lateral.

### 1407-4	MEASUREMENT AND PAYMENT

Electric Service Pole ____ will be measured and paid as the actual number of the appropriate length and class electric service poles installed and accepted.

Electric Service Lateral ____ from service pole to control panel will be measured and paid as the actual number of linear feet of the appropriate size and type service lateral installed and accepted.  Measurement will be along the longest conductor from electrical terminal to electrical terminal.

Payment will be made under:

| Pay Item |  | Pay Unit |
| --- | --- | --- |
| Electric Service Pole ____ |  | Each |
| Electric Service Lateral ____ |  | Linear Foot |

## SECTION 1408

LIGHT CONTROL SYSTEM

1408-1	DESCRIPTION

Furnish and install an entire control system, including enclosure, control panel, photocell, switches, contactors, breakers, terminal blocks, wiring, concrete foundation and lightning arrester.  The control system will be standard electrical components in a stainless steel enclosure mounted on a metal pole with a concrete foundation as shown in the contract.

### 1408-2	MATERIALS

Refer to Division 10.

| Item |  | Section |
| --- | --- | --- |
| Conduit |  | 1091-3 |
| Electrical Junction Box |  | 1091-5 |
| Portland Cement Concrete |  | 1000-2 |
| Wire and Cable |  | 1091-2, 1400-2 |

Provide concrete foundations and wire in accordance with the Specifications.

Use a piece of 4” rigid galvanized steel conduit with threaded conduit cap, embedded in concrete as shown in the plans for mounting the control system

Provide a NEMA type 3R stainless steel enclosure with external stainless mounting flanges, drip shield, back panel and continuous hinge door with a print pocket.  Provide a door closing mechanism interlocked with a flange mounted operator handle to prevent the opening of the door with the service circuit breaker in the ON position, except by use of safety override devices.

Provide an enclosure approximately 36" (h) x 30" (w) x 10" (d) unless noted otherwise in the plans.  Provide only openings necessary for the entrance of conduits as shown in the plans.  Do not use knockouts.  Ensure the enclosure conforms with NEC Article 312 and mount the devices so the NEC clearances will be provided, except use 1.5" where not specified or noted in the tables for minimum wire bending space.

Use galvanized slotted steel framing channel with straps and bolts, sized as shown in the plans for the mounting brackets and hardware for attaching the enclosure to the pole.  Use galvanized finish on the brackets and hardware and coat all field cuts or scratches with organic zinc repair paint.

Provide a polymer concrete (PC) electrical junction box measuring 36" (l) x 24" (w) x 18" (h) (PC36) and meeting Section 1411.

Provide a neutral bar bonded to the panel with sufficient box lug type terminals to accept the required number of wires.

Mount components to the back panel with manufacturer supplied mounting brackets or permanently attached screw studs.

Use a service circuit breaker providing an minimum interrupting rating of 22,000 A.  Provide thermal magnetic, molded case, permanent trip breakers.  Provide multi-tap, solderless, load side box lugs or distribution terminal blocks of the appropriate size.  Use insulating material approved for NEMA 3R applications.  Provide a breaker with a voltage and amperage rating as indicated in the plans.

Provide a single pole, open type control circuit breaker rated at 240 VAC phase to ground with a minimum current interrupting capacity of 5,000 A and a high magnetic trip setting of 15 A.

Provide three 60 A, 4 pole mechanically held contactors that have coil clearing contacts and coil voltage rating as indicated in the plans.  Contactor latching with hooks or 
semi-permanent magnets is unacceptable.

Use a control relay rated 240 VAC with one normally open contact and one normally closed contact and has a continuous load rating and inductive make rating greater than that required by the mechanically held contactor.  Use a coil rated for 240 VAC, 60 Hz.

Use a selector switch which is a heavy duty 3-position maintained contact unit in a surface mount (NEMA 1) enclosure with a legend consisting of On-Off-Auto and having continuous current rating of 10 A at 240 VAC for the contacts.

Use feeder circuit breakers which are rated 14,000 A minimum interrupting capacity and have an open type molded case with a non-adjustable thermal magnetic trip setting as noted in the plans.

Use a photo-control which is the encapsulated cadmium-sulfide type, suitable for use on an operating voltage range of 105 V to 285 V and nominal control voltages of 120 V, 208 V, 240 V and 277 V.  Ensure the control is rated for 1,000 W resistive load or 1,800 V-A of inductive load.  Set the light-level within a range of 1.0 to 3.0 footcandles.  Have internal protection for surges in excess of 2,000 V peak for the control.  Mount a receptacle directly to the top of the enclosure with a weatherproof fitting.  Use controls and receptacles which conform to NEMA Standard C136.10 for roadway lighting equipment.

Use a lightning arrester of the thyrite type, designed to contain and arrest an arc of 10,000 A.  Install the arrester on the load side of the service breaker.

Use terminals and lugs rated for the connection of the appropriate size copper conductors.  All conductors shall be made of copper and neatly wrapped in bundles or run in plastic raceways.

Perform all galvanizing in accordance with Section 1076.

Provide a drawing to scale showing the location, brand and catalog number of each component of the control system for approval.

The completed light control system shall be marked "Suitable for Use as Service Equipment", in a prominent location in the enclosure, in accordance with NEC Article 409.110.  If the control system is not made in a certified UL 60947-4-1A Panel Shop, a third party, recognized by the Department of Insurance as having the authority, shall label the control systems.

### 1408-3	CONSTRUCTION METHODS

Construct the foundation for the control system as shown in the plans with the top of the foundation 3" above finished grade.

Fasten the enclosure to the pole by means of a galvanized bracket assembly as shown in the plans.  Make all cuts square and remove all rough edges.  Have mounting holes match existing mounting holes of the enclosure.

Arrange all conduits entering the enclosure in a neat symmetrical manner and extend directly downward into the foundation.  Install all conduits shown in the plans.  Stub and cap spare conduits for future circuits underground.

Install the PC36 junction box within 2 ft of edge of pad in front of Control System.  Stub all feeder circuit conduits and spare conduits from Control System in this junction box.  See plans for conduit sizes.  Place pull cord in any unused conduits and cap unused conduit in junction box.

Apply 2 coats of organic zinc repair paint to all field cut metal and conduit threads as specified in Article 1076-7.

### 1408-4	MEASUREMENT AND PAYMENT

Light Control Equipment (Type) will be measured and paid as the actual number of the appropriate type light control systems completed and accepted.

Payment will be made under:

| Pay Item |  | Pay Unit |
| --- | --- | --- |
| Light Control Equipment, (Type) ____ |  | Each |

## SECTION 1409

ELECTRICAL DUCT

1409-1	DESCRIPTION

Furnish and install electrical duct including materials, equipment and labor for trenching, jacking, boring or directional boring and backfilling, so electrical circuits may be easily installed, repaired or replaced, and be protected from traffic loading at locations shown in the plans.

### 1409-2	MATERIALS

Refer to Division 10.

| Item |  | Section |
| --- | --- | --- |
| Conduit |  | 1091-3 |

Use electrical duct that is non-metallic rigid PVC heavy wall conduit, HDPE Standard Dimension Ratio (SDR) 13.5 or rigid galvanized steel conduit.

### 1409-3	CONSTRUCTION METHODS

Duct is a passageway for electrical circuits.  Install ducts in accordance with NEC requirements for an approved raceway.  Locate the duct as shown in the plans and at a  depth of at least 30" unless indicated otherwise in the plans.  Locate bore pits outside the clear zone, as defined in the AASHTO Roadside Design Guide.

The lengths noted in the plans are only typical.  Make actual field measurements to place the ends of the duct at the required locations.  Make up lengths of duct with the minimum number of pieces joined together with couplings and solvent as recommended by the manufacturer.

Clean and plug the duct in accordance with Subarticle 1400-4(E).

Plug the duct with oakum or duct seal after feeder circuits in conduit are extended through duct.

Place buried duct in a trench with essentially vertical walls and only wide enough for easy installation of the duct.  Tunneling by hand or other approved methods may be required to install duct beneath existing walks or paved ditches.  Perform backfilling in accordance with Article 300-7.

Jacked duct may be installed by either of the following methods at the Contractor's option, when placement of electrical duct beneath pavement by jacking is noted in the plans.

- The duct may be pushed beneath the pavement through earth without prior construction of an opening.

- A bored opening not more than 1" larger than the outside diameter of the duct may be made by augering and the duct inserted.

- A drilled opening not more than 1" larger than the outside diameter of the duct may be made with a pneumatic vibrating machine and the duct inserted.

- HDPE conduit may be installed in accordance with Subarticle 1715-3(D).

Do not install non-metallic conduit by jacking method (A) as listed above.

If installation of a duct is begun and not completed, plug any opening as directed.  Installation of duct by water jetting will not be acceptable.

At locations where it is indicated in the plans that the duct is to be connected to boxes, foundations, or other raceways, install in accordance with Subarticle 1400-4(E) to provide an approved raceway as specified by the NEC.

Unless otherwise noted in the plans, rigid galvanized steel conduit is intended for use in above ground applications only.

### 1409-4	MEASUREMENT AND PAYMENT

Electrical Duct (Size and Type) will be measured and paid as the actual number of linear feet of duct, measured in place to the nearest whole foot, installed and accepted.

Payment will be made under:

| Pay Item |  | Pay Unit |
| --- | --- | --- |
| Electrical Duct, (Size & Type) ____ |  | Linear Foot |

## SECTION 1410

FEEDER CIRCUITS

1410-1	DESCRIPTION

Furnish and install all conductors and conduit, including tools, equipment, trenching and backfilling to provide electrical circuits at locations shown in the plans.

### 1410-2	MATERIALS

Refer to Division 10.

| Item |  | Section |
| --- | --- | --- |
| Conduit |  | 1091-3 |
| Wire and Cable |  | 1091-2, 1400-2 |

Use UL listed, Type USE wire for feeder circuits in conduit.  The equipment grounding conductor may be bare or insulated.  Use conductors which are copper and in accordance with Subarticle 1400-2(C).  Give careful attention to the required color code.  Do not mark a white conductor in a cable assembly any other color; however, a white conductor may be stripped at all accessible points and used as a bare equipment grounding conductor.

Provide metallic (rigid galvanized steel) and non-metallic (PVC or HDPE) conduit in accordance with the Subarticle 1400-2(B) with the appropriate type being used at locations as shown in the plans.

### 1410-3	CONSTRUCTION METHODS

Install feeder circuits in continuous runs, without splices, except at junction boxes or within light standard bases.

Install conductors in accordance with the Subarticle 1400-4(F) and conduit in accordance with the Subarticle 1400-4(E).

Excavate trenches to depths and widths as shown in the plans with essentially vertical walls and as straight as possible, when underground feeder circuits are required.  Locate underground feeder circuits a minimum of 6 ft back of the face of curb or outside the limits of the paved shoulder and stone base, as directed.  Use care to prevent conflict with existing or future guardrails, sign posts, delineators and similar devices.

Surround the underground feeder circuit in conduit with clean soil and use backfill free of rocks and other objectionable materials which might damage the conduit.  This will require partial backfilling by hand in areas where it is likely that objectionable materials will be included if mechanical methods of backfilling are used.

Perform all necessary search methods, including, but not limited to, use of underground metal detection equipment and excavation equipment, to locate existing electrical duct.  Locate the duct and perform all necessary work including cleaning of the duct before installation of proposed circuits.

When a feeder circuit in conduit passes through electrical duct, make the conduit continuous through the duct unless specifically noted otherwise in the plans.  After feeder circuits in conduit are extended through duct, plug the duct with oakum or duct seal.

When only feeder circuits are required, install the load current carrying conductors and grounding conductors in either existing conduit or conduit installed under other contract items.

When more than one circuit is installed in a single raceway, a single equipment grounding conductor sized as required for the largest circuit may be used without change in the contract unit bid prices.

Multiple circuits may be placed in the same trench if they are grouped and separated a minimum distance of 3".  When more than one circuit is installed in the same trench there will not be any adjustment of the contract unit bid prices.

### 1410-4	MEASUREMENT AND PAYMENT

____ Feeder Circuits will be measured and paid as the actual number of linear feet of each size and type feeder circuit completed and accepted.  Measurement will be to the nearest whole foot from electrical terminal to electrical terminal of the longest load current carrying conductor.

Feeder Circuit in ____ Conduit will be measured and paid as the actual number of linear feet of each size and type feeder circuit completed and accepted.  Measurement will be to the nearest whole foot from electrical terminal to electrical terminal of the longest load current carrying conductor.

Payment will be made under:

| Pay Item |  | Pay Unit |
| --- | --- | --- |
| ____ Feeder Circuit |  | Linear Foot |
| ____ Feeder Circuit in ____ Conduit |  | Linear Foot |

## SECTION 1411

ELECTRICAL JUNCTION BOXES

1411-1	DESCRIPTION

Provide junction boxes made from fiberglass reinforced polymer concrete and cast-metal boxes encased in concrete of the appropriate type at locations noted in the plans, complete with all necessary covers, conduits, duct and hardware, in accordance with the contract.

### 1411-2	MATERIALS

Refer to Division 10.

| Item |  | Section |
| --- | --- | --- |
| Backfill |  | 545, 1005 |
| Electrical Junction Boxes |  | 1091-5 |

Provide a polymer concrete junction box which is open bottom with a foot.  Provide a standard “Electric” logo on the cover unless specifically noted otherwise in the plans.  Backfill beneath and around the boxes using ABC in conformance with Section 1005.

### 1411-3	CONSTRUCTION METHODS

Install conduits and duct before the polymer concrete (PC) boxes are set in place.  Do not rest the bottom of the box directly on conduits, ducts or cables.

Place the top of the box on the same grade as the surrounding area.  Perform backfilling with sufficient care that no part of the junction box, conduit or duct is displaced or moved out of alignment.  Backfill beneath and around the box to at least 12" using #67 washed stone aggregates in conformance with Section 545 and Section 1005.

Locate junction boxes for best routing of conduit and duct and to minimize drainage problems.  Do not locate boxes in useable shoulders or pavements or other areas where they may be subjected to traffic loadings.

Stub the ends of conduit and duct up vertical as near the top of the box as practical and seal.  Arrange wiring so that it will not lay in the bottom of the box.

Install cast-metal (BR) boxes and arrange conduits and ducts to best fit field conditions.  During the construction of the median barrier reinforcement, accurately space and securely attach Type BR junction boxes and conduits inside the reinforcement.  Bond junction box to the reinforcement in accordance with NEC Article 250.52.  Place boxes with covers flush with surface of concrete (generally traffic side of median barrier).

Place mastic between the cast metal box frame and the cast concrete barrier, as shown on plans to allow easy replacement of the frame.

### 1411-4	MEASUREMENT AND PAYMENT

Electrical Junction Boxes ____ will be measured and paid as the actual number of the appropriate type and size junction boxes installed and accepted.  Payment for the conduit, duct and wiring will be paid under other contract items.  Items used for splicing are incidental to the junction boxes.

Payment will be made under:

| Pay Item |  | Pay Unit |
| --- | --- | --- |
| Electrical Junction Boxes ____ |  | Each |

## SECTION 1412

UNDERPASS LIGHTING

1412-1	DESCRIPTION

Furnish and install wall mounted and/or pendant mounted luminaires with electrical circuitry, for underpass lighting at locations shown in the plans.  Work includes, but is not limited to, furnishing and installing underpass luminaires with lamp, ballast and mounting hardware as well as furnishing and installing circuit breakers and enclosure, pull boxes, conduit, conductors, expansion fittings, anchors, straps and ground rod.

### 1412-2	MATERIALS

Refer to Division 10.

| Item |  | Section |
| --- | --- | --- |
| Conduit |  | 1091-3 |
| Wire and Cable |  | 1091-2 |

Use luminaires that are listed as “Suitable for Wet Locations” according to UL Standard 1572, with sealed and filtered optical assemblies.  Use high power factor ballasts that are completely pre-wired integral units, for reliable starting and operating of high pressure sodium lamps 
at -40°F ambient temperature.  Use heavy-duty mogul base lamp sockets, with split shell tempered brass lamp grips and a free-floating, spring-loaded center contact.  Use the luminaire type, wattage, voltage and IES illumination distribution pattern as shown in the plans.

Provide Type WM luminaires that are wall mounted, with cast aluminum housing painted with premium quality gray or dark bronze paint.  Provide a prewired ballast and terminal board assembly and cast aluminum side-hinged door with glass refractor.  Use the same color Type WM luminaires throughout the project.  Provide factory installed mounting holes in the back and conduit entrances in the sides and top.  Provide a formed aluminum reflector and socket assembly, with a chemically-bonded, lightweight, non-breakable glass finish, which is removable with only a screwdriver.

Provide Type PM luminaires that are a pendant mounted assembly of ballast, optical and mounting components, including a safety chain and hanging hardware.  Provide a die-cast aluminum ballast housing with gray paint finish, with a prewired ballast assembly and an external quick electrical disconnect receptacle for attachment of hanging hardware.  Provide a faceted aluminum reflector with a hard glasslike highly reflective corrosion resistant finish and a lightly diffused refractor made of UV stabilized, injection molded, prismatic, heat-resistant acrylic.  Provide hinges and stainless steel, over-center, vibration-resistant spring latches for easy access to the lamp and clamping of the gasket between the refractor and ballast housing.

Use a 3/4" rigid galvanized steel conduit with a hook and power cord entrance as the pendant.  Provide a 3-conductor Type SO power cord and a 3/4" female threaded wiring compartment with quick electrical disconnects, to attach the ballast housing to the pendant as shown in the plans.

Use galvanized weldless forged steel eye-nuts that comply with Federal 
Specification WW-H-171E (Type 17), or Manufacturers Standardization Society SP-69-2003 (Type 17).  Attach eye nuts to galvanized steel or stainless steel threaded rod anchored to the bridge deck with adhesive anchors.  Use galvanized steel or stainless steel safety chain, 
S-hooks and lock nuts.

Use conduit and wire in accordance with Article 1400-2 and gasketed PVC junction boxes as shown in the plans.

Use a 2-pole, 480 VAC, 20 A circuit breaker with an interrupting capacity of at least 
14,000 A, installed in a NEMA 3R enclosure.  The enclosure should be primed and painted with a premium grade exterior paint before installation to increase corrosion resistance.  Install an equipment ground bar and provide a lock in accordance with Article 1400-8.

### 1412-3	CONSTRUCTION METHODS

Mount luminaires as shown in the plans.  Use galvanized steel or stainless steel clamps and attachment hardware.

Install circuitry in accordance with Article 1400-4.

### 1412-4	MEASUREMENT AND PAYMENT

Underpass Luminaires ____ will be measured and paid as the actual number installed and accepted.

Underpass Circuitry at ____ will be paid at the contract lump sum price for underpass circuitry at the appropriate location.

Payment will be made under:

| Pay Item |  | Pay Unit |
| --- | --- | --- |
| Underpass Luminaires ____ |  | Each |
| Underpass Circuitry at ____ |  | Lump Sum |

## SECTION 1413

PORTABLE CONSTRUCTION LIGHTING

1413-1	DESCRIPTION

Furnish, operate and maintain everything necessary to provide lighting for compliance with Article 105-14 Night Work requirement for artificial lighting.

### 1413-2	MATERIALS

Furnish all lighting equipment as required and retain after the work is completed.  Material and/or equipment is not required to be new but shall be in good operating condition and in compliance with applicable safety and design codes.

Submit, for the review and approval catalog cuts giving the specific brand names, model numbers and ratings of the lighting equipment.  Include in the submittals power ratings and photometric data.  Allow 40 days for review of the submittals.  Do not begin night work without approval of the equipment and/or materials.

### 1413-3	TOWER LIGHT

Use tower lights which consist of mercury vapor, metal halide, high pressure sodium or low pressure sodium fixtures mounted on a tower approximately 30 ft in height.  Use tower light fixtures which are heavy duty flood, area, or roadway style with wide beam spread, have an output of 50,000 lumens minimum, have the combined outputs of all fixtures on each tower light not exceed 460,000 lumens, and are weatherproof and supplied with attached waterproof power cord and plug.  Use a sturdy tower which is freestanding without the aid of guy wires or bracing.  Provide sufficient capacity in the power supply to operate the light(s) and locate it for the shortest safe routing of cables to the fixtures.  A tower light consisting of the combined fixture(s), tower and power supply is preferred.

Provide tower lights of sufficient wattage and/or quantity to provide an average maintained horizontal illuminance greater than 20 footcandles over the work area.

Aim and position the lights to illuminate the area for construction work.  Make sure that there is not any disabling glare to the motorist.  In no case should the main beam of the light be aimed higher than 60° above straight down.  The lights should be set as far from traffic as practical and aimed in the direction of, or normal to, the traffic flow.

### 1413-4	MACHINE LIGHTS

Use machine lights which have mercury vapor, metal halide, high pressure sodium or low pressure sodium conventional roadway enclosed fixtures mounted on supports attached to the construction machine at a height of approximately 13 ft.  Use fixtures for machine lights which have light output between 22,000 and 50,000 lumens.  Use a power supply with sufficient capacity to operate the light(s) and securely mount on the machine.  Perform electrical grounding of generators to frames of machines on which they are mounted in conformance with the NEC.

Use machine light fixtures with sufficient wattage and/or quantity to provide an average maintained horizontal illuminance greater than 10 footcandles on the machine and the surrounding work area.  Machine lights are in addition to conventional automotive type headlights which are necessary for maneuverability.

Balloon lights are an acceptable alternate luminaire for machine lights.

### 1413-5	CONSTRUCTION METHODS

Use tower lights when the night work is confined to a fairly small area and is essentially a stationary operation.  Space tower lights no closer than 100 ft apart and no further than 300 ft apart.  Actual spacing will be determined by approved equipment.  At any spacing, the required 20 footcandles of light will be the determining factor.

Use machine lights when the night work is not confined to a small area and is essentially a continuous moving construction operation.

Tower lights may be provided instead of machine lights upon approval by the Engineer.  Use of tower lights instead of machine lights will be considered when the number of machines, type of work, or need for inspection justify their use as decided by the Engineer.

Illuminate the work area where traffic control devices are being set up or repositioned at night.

The work areas to be illuminated are the areas where construction equipment and labor are in operation and may be different from the work areas shown in the plans.

Illuminate a large enough work area so that the movements of all personnel and equipment engaged in the work will be contained in the area.

Provide sufficient fuel, spare lamps, generators and personnel qualified to operate the lights to assure that they will be maintained in operation during night work.

Existing streetlights do not eliminate the requirement for the Contractor to provide lighting.  Consideration may be given to the amount of illumination provided by existing lights in determining the wattage and/or quantity of lights to be provided.

### 1413-6	MEASUREMENT AND PAYMENT

Portable Lighting provided by tower and machine lights will be paid only when a significant amount of nighttime work is explicitly required and a pay item for portable lighting has been included in the contract.  Otherwise, portable construction lighting will be incidental to other contract items and no direct payment will be made.

The aggregate amount to be paid on each partial payment estimate will be equal to the percentage that the item of Portable Lighting is complete as estimated by the Engineer.

Payment will be made under:

| Pay Item |  | Pay Unit |
| --- | --- | --- |
| Portable Lighting |  | Lump Sum |